Commercial Building Data Collection Checklist

2009 International Energy Conservation Code

Building ID:       		Climate Zone:

Date:       		Name of Evaluator(s):

Building Contact:  Name:       		Phone:       		Email:

Building Name & Address:       		Conditioned Floor Area:        	ft2

State:       		County:       		Jurisdiction:

Compliance Approach (check all that apply):    Prescriptive     Trade-Off     Performance

Compliance Software (if used):       		Green/Above-Code Program:

Building Use: 	 Office	 Retail/Mercantile	 Warehouse/Storage	 Education/School	 Lodging/Hotel/Motel

Restaurant/Dining/Fast Food	 Public Assembly/Religious	 Healthcare	 High-Rise Residential	 Other

Building Ownership:	 State-owned	 Local government-owned	 National account	 Speculative	 Private	 Other

Project Type:	 New Building	 Existing Building Addition	 Existing Building Renovation	Valuation (If Renovation): $

| 2009 IECC Section # | Plan Review | Complies | Comments/Assumptions |
| --- | --- | --- | --- |
|  |  | Y | N | N/A |  |
| 103.2 [PR1]1 | Plans and/or specifications provide all information with which compliance can be determined for the building envelope and delineate and document where exceptions to the standard are claimed. |  |  |  |  |
| 103.2 [PR2]1 | Plans, specifications, and/or calculations provide all information with which compliance can be determined for the mechanical systems and equipment and delineate and document where exceptions to the standard are claimed. |  |  |  |  |
| 103.2 [PR3]1 | Plans, specifications, and/or calculations provide all information with which compliance can be determined for the service water heating systems and equipment and delineate and document where exceptions to the standard are claimed. |  |  |  |  |
| 103.2 [PR4]1 | Plans, specifications, and/or calculations provide all information with which compliance can be determined for the lighting and electrical systems and equipment and delineate and document where exceptions to the standard are claimed. Information provided should include interior and exterior lighting power calculations, wattage of bulbs and ballasts, transformers and control devices. |  |  |  |  |

# Additional Comments/Assumptions:

General building information only required if different than above	Building ID:

Date:       		Name of Evaluator(s):

Building Contact:  Name:       		Phone:       		Email:

Building Name & Address:       		Conditioned Floor Area:        	ft2

Compliance Approach (check all that apply):    Prescriptive     Trade-Off     Performance

Compliance Software (if used):       		Green/Above-Code Program:

| 2009 IECC Section # | Footing / Foundation Inspection | Verified Value | Complies | Comments/Assumptions |
| --- | --- | --- | --- | --- |
|  |  |  | Y | N | N/A |  |
| 502.2.4 [FO1]2 | Below-grade wall insulation R-value. | R- |  |  |  |  |
| 303.2 [FO2]2 | Below-grade wall insulation installed per manufacturer’s instructions. |  |  |  |  |  |
| 502.2.6 [FO3]2 | Slab edge insulation R-value. | R- Unheated Heated |  |  |  |  |
| 303.2 [FO4]2 | Slab edge insulation installed per manufacturer’s instructions. |  |  |  |  |  |
| 502.2.6 [FO5]2 | Slab edge insulation depth/length. | ft |  |  |  |  |
| 303.2.1 [FO6]1 | Exterior insulation protected against damage, sunlight, moisture, wind, landscaping and equipment maintenance activities and should extend >=6 in. below grade. |  |  |  |  |  |
| 503.2.7 [FO8]1 | Piping, ducts and plenum are insulated and sealed when installed in or under a slab. | R- |  |  |  |  |
| 503.2.4.5 [FO9]3 | Freeze protection and snow/ice melting system sensors for future connection to controls. |  |  |  |  |  |
| 504.5 [FO10]1 | Any recirculating SWH piping in or under slab is insulated. | R- |  |  |  |  |

# Additional Comments/Assumptions:

General building information only required if different than above	Building ID:

Date:       		Name of Evaluator(s):

Building Contact:  Name:       		Phone:       		Email:

Building Name & Address:       		Conditioned Floor Area:        	ft2

Compliance Approach (check all that apply):    Prescriptive     Trade-Off     Performance

Compliance Software (if used):       		Green/Above-Code Program:

| 2009 IECC Section # | Framing / Rough-In Inspection | Verified Value | Complies | Comments/Assumptions |
| --- | --- | --- | --- | --- |
|  |  |  | Y | N | N/A |  |
| 502.4.1, 502.4.2 [FR1]3 | Fenestration meets maximum air leakage requirements. | cfm/ ft2 |  |  |  |  |
| 502.4.1, 502.4.2 [FR2]3 | Doors meet maximum air leakage requirements. | cfm/ ft2 |  |  |  |  |
| 502.4.1, 502.4.2 [FR3]3 | Fenestration and doors labeled for air leakage. |  |  |  |  |  |
| 502.4.7 [FR4]3 | Vestibules installed per approved plans. |  |  |  |  |  |
| 502.2.1 [FR5]1 | Roof insulation R-value. | R- Above deck Metal Attic |  |  |  |  |
| 303.2 [FR6]1 | Roof insulation R-value installed per manufacturer’s instructions. |  |  |  |  |  |
| 502.3.1, 502.1.1 [FR7]1 | Performance compliance approach submitted for vertical fenestration area >40% or skylight area >3%. |  |  |  |  |  |
| 502.3.2 [FR8]1 | Vertical fenestration U-Factor. | U- |  |  |  |  |
| 502.3.2 [FR9]1 | Skylight fenestration U-Factor. | U- |  |  |  |  |
| 502.3.2 [FR10]1 | Vertical fenestration SHGC value. | SHGC: |  |  |  |  |
| 502.3.2 [FR11]1 | Skylight SHGC value. | SHGC: |  |  |  |  |
| 303.1.3 [FR12]2 | Fenestration products rated in accordance with NFRC. |  |  |  |  |  |
| 303.1.3 [FR13]1 | Fenestration products are certified as to performance. Labels or certificates provided. |  |  |  |  |  |
| 502.3.2, 502.4.1, 502.4.2 [FR14] 2 | U-factor of opaque doors associated with the building thermal envelope meets requirements. | U- Swinging Nonswinging |  |  |  |  |

# Additional Comments/Assumptions:

General building information only required if different than above	Building ID:

Date:       		Name of Evaluator(s):

Building Contact:  Name:       		Phone:       		Email:

Building Name & Address:       		Conditioned Floor Area:        	ft2

Compliance Approach (check all that apply):    Prescriptive     Trade-Off     Performance

Compliance Software (if used):       		Green/Above-Code Program:

| 2009 IECC Section # | Plumbing Rough-In Inspection | Complies | Comments/Assumptions |
| --- | --- | --- | --- |
|  |  | Y | N | N/A |  |
| 504.5 [PL1]2 | Piping for recirculating and non-recirculating service hot-water systems insulated. |  |  |  |  |
| 504.3 [PL2] 3C | Temperature controls installed on service water heating systems <=110 ºF for intended use serving dwelling units and <=90 ºF serving other occupancies. |  |  |  |  |
| 504.6 [PL3]1 | Automatic time switches installed to automatically switch off the recirculating hot-water system or heat trace. |  |  |  |  |
| [504.4 [PL4]3 | Heat traps installed on non-circulating storage water tanks. |  |  |  |  |

# Additional Comments/Assumptions:

General building information only required if different than above	Building ID:

Date:       		Name of Evaluator(s):

Building Contact:  Name:       		Phone:       		Email:

Building Name & Address:       		Conditioned Floor Area:        	ft2

Compliance Approach (check all that apply):    Prescriptive     Trade-Off     Performance

Compliance Software (if used):       		Green/Above-Code Program:

| 2009 IECC Section # | Mechanical Rough-In Inspection | Verified Value | Complies | Comments/Assumptions |
| --- | --- | --- | --- | --- |
|  |  |  | Y | N | N/A |  |
| 503.2.3 [ME1]2 | HVAC equipment efficiency verified. | Efficiency: |  |  |  |  |
| Table 503.2.3(3) [ME2] 3 | PTAC and PTHP with sleeves 16 in by 42 in. labeled for replacement only. |  |  |  |  |  |
| 502.4.5 [ME3] 3 | Stair and elevator shaft vents have motorized dampers that automatically close. |  |  |  |  |  |
| 502.4.5, 503.2.4.4 [ME4] 3 | Outdoor air and exhaust systems have motorized dampers that automatically shut when not in use and meet maximum leakage rates. Check gravity dampers where allowed. |  |  |  |  |  |
| 503.2.5.1 [ME6]1 | Demand control ventilation provided for spaces >500 ft2 and >40 people/1000 ft2 occupant density and served by systems with air side economizer, auto modulating outside air damper control or design airflow >3,000 cfm. |  |  |  |  |  |
| 503.2.7 [ME8]2 | HVAC ducts and plenums insulated. | R- |  |  |  |  |
| 503.2.8 [ME9]2 | HVAC piping insulation thickness. | in. |  |  |  |  |
| 503.2.7.1 [ME10] 2 | Ducts and plenums sealed based on static pressure and location. |  |  |  |  |  |
| 503.2.7.1.3 [ME11] 3 C | Ductwork operating >3 in. water column is air leakage tested. |  |  |  |  |  |
| 503.3.1, 503.4.1 [ME12]1 | Air economizers provided where required, meet the requirements for design capacity, control signal, and high-limit shut-off and integrated economizer control. |  |  |  |  |  |
| 502.4.5, 503.2.4.4 [ME13] 2 | Return air and outdoor air dampers meet minimum air leakage requirements. |  |  |  |  |  |
| 503.3.1 [ME14]1 | Means provided to relieve excess outside air. |  |  |  |  |  |
| 503.4.5 [ME17] 1 | Zone controls can limit simultaneous heating and cooling and sequence heating and cooling to each zone. |  |  |  |  |  |
| 503.4.3.3 [ME18] 2C | Hydronic heat pump systems connected to a common water loop meet heat rejection and heat addition requirements. |  |  |  |  |  |
| 503.2.9.1 [ME41iecc]3 | Air outlets and zone terminal devices have means for air balancing. |  |  |  |  |  |
| 503.2.9.2 [ME42iecc]3 | HVAC hydronic heating and cooling coils have means to balance and have pressure test connections. |  |  |  |  |  |
| 503.2.10.1 [ME40iecc]1 | HVAC fan systems >5 hp meet fan power limitation. |  |  |  |  |  |
| 503.2.10.2 [ME21] 2 | HVAC fan motors not larger than the first available motor size greater than the bhp. | bhp: |  |  |  |  |
| 503.4.2 [ME22] 2C | VAV fan motors ≥10 hp to be driven by mechanical or electrical variable speed drive, or have a vane-axial fan with variable pitch blades, or have controls or devices to limit fan motor demand to <30% of design wattage at 50% design air volume at static pressure of 1/3 total rated static pressure of the fan. | VSD Vane axial fan Other |  |  |  |  |
| 503.4.2 [ME24] 2C | Reset static pressure setpoint for DDC controlled VAV boxes reporting to central controller based on the zones requiring the most pressure. |  |  |  |  |  |
| 503.4.3.5 [ME26] 3C | Reduce flow in pumping systems of any size to multiple chillers or boilers when others are shut down. |  |  |  |  |  |
| 503.4.3.4 [ME27] 3C | Temperature reset by representative building loads in pumping systems >10 hp for chiller and boiler systems > 300,000 Btu/h. |  |  |  |  |  |
| 503.4.3.3.3 [ME28] 3 C | Two-position automatic valve interlocked to shut off water flow when hydronic heat pump with pumping system >10 hp is off. |  |  |  |  |  |
| 503.4.4 [ME29] 3C | Fan systems with motors ≥7.5 hp associated with heat rejection equipment to have capability to operate at 2/3 of full-speed and auto speed controls to control the leaving fluid temp or condensing temp/pressure of heat rejection device. |  |  |  |  |  |
| 503.2.6 [ME30]1 | Exhaust air energy recovery on systems ≥ 5,000 cfm and 70% of design supply air. |  |  |  |  |  |
| 503.4.6 [ME31] 3C | Condenser heat recovery system that can heat water to 85 ºF or provide 60% of peak heat rejection is installed for preheating of service hot water in 24/7 facility, water cooled systems reject >6 MMBtu, SHW load ≥1 MMBtu. |  |  |  |  |  |
| 503.2.11 [ME34] 3 | Unenclosed spaces that are heated use only radiant heat. |  |  |  |  |  |
| 502.4.4 [ME35]1 C | Hot gas bypass on cooling systems limited to: ≤240 kBtu/h – 50% >240 kBtu/h – 25% |  |  |  |  |  |
| 504.2 [ME36]2C | Service water heating equipment meets efficiency requirements. |  |  |  |  |  |

# Additional Comments/Assumptions:

General building information only required if different than above	Building ID:

Date:       		Name of Evaluator(s):

Building Contact:  Name:       		Phone:       		Email:

Building Name & Address:       		Conditioned Floor Area:        	ft2

Compliance Approach (check all that apply):    Prescriptive     Trade-Off     Performance

Compliance Software (if used):       		Green/Above-Code Program:

| 2009 IECC Section # | Rough-In Electrical Inspection | Complies | Comments/Assumptions |
| --- | --- | --- | --- |
|  |  | Y | N | N/A |  |
| 505.2.2.2 [EL1] 2 | Automatic lighting control to shut off all building lighting installed in buildings >5,000 ft2. |  |  |  |  |
| 505.2.1 [EL2] 2 | Independent lighting control installed per approved lighting plans and all manual control readily accessible and visible to occupants. |  |  |  |  |
| 505.2.2.1 [EL10iecc] 1 | Lighting controls installed to uniformly reduce the lighting load by at least 50%. |  |  |  |  |
| 505.2.4 [EL3] 2 | Automatic lighting controls for exterior lighting installed. |  |  |  |  |
| 505.2.3 [EL4] 1 | Verify separate lighting control devices for specific uses installed per approved lighting plans. |  |  |  |  |
| 505.3 [EL5] 3 | Ballasted one and three lamp fixtures with >30 W/lamp have two lamp tandem wired ballasts when >2 fixtures in same space on same control. |  |  |  |  |
| 505.4 [EL6] 1 | Exit signs do not exceed 5 watts per face. |  |  |  |  |
| 505.6.1 [EL7] 1 | Exterior grounds lighting over 100 W provides >60 lm/W unless on motion sensor or fixture is exempt from scope of code or from external LPD. |  |  |  |  |

# Additional Comments/Assumptions:

General building information only required if different than above	Building ID:

Date:       		Name of Evaluator(s):

Building Contact:  Name:       		Phone:       		Email:

Building Name & Address:       		Conditioned Floor Area:        	ft2

Compliance Approach (check all that apply):    Prescriptive     Trade-Off     Performance

Compliance Software (if used):       		Green/Above-Code Program:

| 2009 IECC Section # | Insulation Inspection | Verified Value | Complies | Comments/Assumptions |
| --- | --- | --- | --- | --- |
|  |  |  | Y | N | N/A |  |
| 502.4.3 [IN1] 1 | All sources of air leakage in the building thermal envelope are sealed, caulked, gasketed, weather stripped or wrapped with moisture vapor-permeable wrapping material to minimize air leakage. |  |  |  |  |  |
| 502.2.1 [IN2] 1 | Roof insulation R-value. | R- |  |  |  |  |
| 303.2 [IN3] 1 | Roof insulation installed per manufacturer’s instructions. |  |  |  |  |  |
| 502.2.3 [IN6] 1 | Above-grade wall insulation R-value. | R- Mass Metal Steel Wood |  |  |  |  |
| 303.2 [IN7] 1 | Above-grade wall insulation installed per manufacturer’s instructions. |  |  |  |  |  |
| 502.2.5 [IN8] 2 | Floor insulation R-value. | R- Mass Steel Wood |  |  |  |  |
| 303.2 [IN9] 2 | Floor insulation installed per manufacturer’s instructions. |  |  |  |  |  |
| 303.1.1, 303.1.1.1 [IN10] 2 | Building envelope insulation is labeled with R-value or insulation certificate providing R-value and other relevant data. |  |  |  |  |  |
| 303.2.1 [IN14] 2 | Exterior insulation is protected from damage with a protective material. |  |  |  |  |  |
| 502.2.1 [IN17] 3 | Insulation intended to meet the roof insulation requirements not installed on top of a suspended ceiling. |  |  |  |  |  |

# Additional Comments/Assumptions:

General building information only required if different than above	Building ID:

Date:       		Name of Evaluator(s):

Building Contact:  Name:       		Phone:       		Email:

Building Name & Address:       		Conditioned Floor Area:        	ft2

Compliance Approach (check all that apply):    Prescriptive     Trade-Off     Performance

Compliance Software (if used):       		Green/Above-Code Program:

| 2009 IECC Section # | Final Inspection | Complies | Comments/Assumptions |
| --- | --- | --- | --- |
|  |  | Y | N | N/A |  |
| 502.4.6 [FI1] 1 | Weatherseals installed on all loading dock cargo doors in all zones. |  |  |  |  |
| 503.2.4.1 [FI2] 2 | Heating and cooling to each zone is controlled by a thermostat control. |  |  |  |  |
| 503.2.4.2, 503.2.4.3 [FI3] 2 | Temperature controls have the following features: dead band controls, setpoint overlap restrictions, off-hour controls, automatic shutdown, setback controls. |  |  |  |  |
| 503.2.4.1.1 [FI5] 3 | Heat pump controls prevent supplemental electric resistance heat from coming on when not needed. |  |  |  |  |
| 502.4.8 [FI20iecc]3 | Recessed luminaires in thermal envelope to limit infiltration and be IC rated and labeled. Seal between interior finish and luminaire housing. |  |  |  |  |
| 503.2.2 [FI21iecc]3 | HVAC systems and equipment capacity does not exceed calculated loads. |  |  |  |  |
| 504.3 [FI11] 3 | Public lavatory faucet water temperature not greater than 110 oF. |  |  |  |  |
| 504.5 [FI19iecc] 2 | Insulate automatic circulating hot water systems and 1st eight feet of non-circulating systems without integral heat traps. |  |  |  |  |
| 504.7.1 [FI13] 3C | Pool heaters are equipped with on/off switch and no continuous burning pilot light. |  |  |  |  |
| 504.7.3 [FI4]2C | Pool covers are provided for heated pools and pools heated to >90˚F have a cover >R-12. |  |  |  |  |
| 504.7.2 [FI15]3C | Time switches are installed on all pool heaters and pumps. |  |  |  |  |
| 503.2.9.3 [FI17]3 | Furnished O&M instructions for systems and equipment to the building owner or designated representative. |  |  |  |  |
| 505.5, 505.6 [FI18] 1 | Installed lamps and fixtures are consistent with what is shown on the approved lighting plans. |  |  |  |  |

# Additional Comments:

| KEY | 1 | High Impact (Tier 1) | 2 | Medium Impact (Tier 2) | 3 | Low Impact (Tier 3) | C | Complex Mechanical |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Evaluator Assessment

Please provide a general description of what was discovered during the onsite evaluation, and a professional estimate of what you feel the compliance rating should be, regardless of the individual metrics scored above. Include your assessment of the most impactful energy requirements for this particular building.